## OVERALL ENGINEER NOTES
OVERALL ENGINEER NOTES: (Notes to the Designer NOT to be included the construction documents.)
1. THESE TABLES WERE DEVELOPED BY THE SEAO SPECIAL INSPECTION COMMITTEE. THEY ARE BASED ON THE OSSC 2019 AND REFERENCE DOCUMENTS. PLEASE CONTACT ONE OF THE SEAO SPECIAL INSPECTION COMMITTEE MEMBERS IF YOU FIND ERRORS OR ITEMS THAT ARE UNCLEAR.
2. REVIEW TABLES WITH GENERAL STRUCTURAL NOTES AND PROJECT SPECIFICATIONS. MANY SPECIFICATION SECTIONS INCLUDE INSPECTION AND TESTING REQUIREMENTS. AVOID REDUNDANT INFORMATION.
3. REVIEW ALL TABLES TO DETERMINE WHICH APPLY TO YOUR PROJECT. REMOVE TABLES THAT DO NOT APPLY. CONSIDER REVIEWING MULTIPLE TIMES DURING THE DESIGN PHASE OF PROJECT. TABLE NUMBERS ARE REFERENCED WITHIN THE TABLES. IF RENUMBERING TABLES MAKE SURE ALL TABLE REFERENCES ARE UPDATED. IDENTIFY INSPECTION POINTS, FREQUENCY, TYPE AND EXTENT OF SPECIAL INSPECTIONS.
4. SEE TABLE SPECIFIC ENGINEERING NOTES FOR ADDITIONAL GUIDANCE, LOCATED TO RIGHT SIDE OF TABLES USING BLUE TEXT.
5. REVIEW USE OF PERIODIC INSPECTION. PROVIDE FURTHER DEFINITION WHERE EXTENT, FREQUENCY AND TYPE OF INSPECTIONS FOR EACH MATERIAL OR TYPE OF CONSTRUCTION ARE SPECIFICALLY DEFINED.
6. CONTRACTOR RESPONSIBILITY PROGRAM APPLIES ONLY TO BUILDINGS REQUIRING SPECIAL INSPECTIONS FOR WIND OR SEISMIC RESISTANCE. REFERENCE OSSC SECTION 1704.4, 1705.11 AND 1705.12
7. CODE ALLOWS FOR SPECIAL INSPECTIONS TO BE OMITTED FOR CONSTRUCTION OF A MINOR NATURE. REFERENCE OSSC 1704.2.
8. SEE GENERAL STRUCTURAL NOTES FOR STRUCTURAL OBSERVATIONS. STRUCTURAL OBSERVATIONS ARE NOT ADDRESSED IN THESE TABLES.
9. STEEL INSPECTION REQUIREMENTS ARE FROM BOTH THE OSSC AND THE REFERENCED AISC 341 AND 360 PER OSSC SECTION 1705.2.1 AND 1705.11.1. OSSC TABLES AND AISC TABLE UTILIZE DIFFERENT NOMENCLATURE REQUIRING EXPANDED TABLES. OTHER STATES, INCLUDING CALIFORNIA AND WASHINGTON, ADOPTED THE IBC'S REQUIREMENTS WHICH USE INSPECTION REQUIREMENTS FROM AISC ALONE FOR STEEL.
10. AISC REQUIREMENTS FOR STEEL INSPECTIONS ARE INTENDED TO SHIFT SOME OF THE INSPECTION REQUIREMENTS TO THE FABRICATOR AND ERECTOR. SEE AISC 360 N2 AND AISC 341 J FOR "FABRICATOR AND ERECTOR QUALITY CONTROL PROGRAM" REQUIREMENTS.
11. SEE 1704.2.5.1 FOR FABRICATION AND IMPLEMENTATION PROCEDURES.

## INSPECTION NOTES
STATEMENT OF SPECIAL INSPECTION NOTES:
1. | SPECIAL INSPECTIONS SHALL CONFORM TO SECTION 1705 OF THE 2019 OSSC, CONTRACT DOCUMENTS AND APPROVED SUBMITTALS. REFER TO SPECIAL INSPECTION AND TESTING TABLES FOR PROJECT REQUIREMENTS.
2. | SPECIAL INSPECTIONS AND ASSOCIATED TESTING SHALL BE PERFORMED BY AN APPROVED ACCREDITED INDEPENDENT AGENCY MEETING THE REQUIREMENTS OF ASTM E329 (MATERIALS). THE INSPECTION AND TESTING AGENCY SHALL FURNISH TO THE STRUCTURAL ENGINEER ARCHITECT A COPY OF THEIR SCOPE OF ACCREDITATION. SPECIAL INSPECTORS SHALL BE APPROVED BY THE BUILDING OFFICIAL. WELDING INSPECTORS SHALL BE QUALIFIED PER SECTION 6.1.4.1(1) OF AWS D1.1.
3. | THE SPECIAL INSPECTOR SHALL OBSERVE THE INDICATED WORK FOR COMPLIANCE WITH THE APPROVED CONSTRUCTION DOCUMENTS. ALL DISCREPANCIES SHALL BE BROUGHT TO THE ATTENTION OF THE CONTRACTOR FOR CORRECTION AND NOTED IN THE INSPECTION REPORTS.
4. | THE SPECIAL INSPECTOR AND GEOTECHNICAL ENGINEER SHALL FURNISH INSPECTION REPORTS FOR EACH INSPECTION TO THE BUILDING OFFICIAL, STRUCTURAL ENGINEER, ARCHITECT, CONTRACTOR, AND OWNER. THE SPECIAL INSPECTION AGENCY SHALL SUBMIT A FINAL REPORT STATING THAT THE WORK REQUIRING SPECIAL INSPECTION WAS INSPECTED AND IS IN CONFORMANCE WITH THE APPROVED CONSTRUCTION DOCUMENTS AND THAT ALL DISCREPANCIES NOTED IN THE INSPECTION REPORTS HAVE BEEN CORRECTED.
5 | QUALITY ASSURANCE (QA) IS REQURIED FOR STRUCTURAL STEEL ITEMS PER AISC 360 AND 341 UNLESS SPECIFICALLY NOTED OTHERWISE. QUALITY CONTROL (QC) TO BE PROVIDED BY THE FABRICATOR, ERECTOR OR OTHER RESPONSIBLE CONTRACTOR AS APPLICABLE. CONTRACTOR AND SPECIAL INSPECTOR TO DOCUMENT QUALITY CONTROL AS REQUIRED IN AISC 360 SECTION N3 AND AISC 341 SECTION J2.
6 | INSPECTION TYPES:
CONTINUOUS : THE FULL-TIME OBSERVATION OF WORK REQUIRING SPECIAL INSPECTION BY AN APPROVED SPECIAL INSPECTOR WHO IS PRESENT IN THE AREA WHERE THE WORK IS BEING PERFORMED.
PERIODIC : THE PART-TIME OR INTERMITTENT OBSERVATION OF WORK REQUIRING SPECIAL INSPECTION BY AN APPROVED SPECIAL INSPECTOR WHO IS PRESENT IN THE AREA WHERE THE WORK HAS BEEN OR IS BEING PERFORMED AND AT THE COMPLETION OF THE WORK.
OBSERVE : OBSERVE THESE FUNCTIONS ON A RANDOM, DAILY BASIS. OPERATIONS NEED NOT BE DELAYED PENDING OBSERVATIONS.
PERFORM : INSPECTIONS SHALL BE PERFORMED PRIOR TO THE FINAL ACCEPTANCE OF THE ITEM.
7 | PERFORM INSPECTION PRIOR TO FINAL ACCEPTANCE OF THE ITEM FOR TEN WELDS TO BE MADE BY A GIVEN WELDER, WITH THE WELDER DEMONSTRATING UNDERSTANDING OF REQUIREMENTS AND POSSESSION OF SKILLS AND TOOLS TO VERIFY THESE ITEMS, THE PERFORM DESIGNATION OF THIS TASK SHALL BE REDUCED TO OBSERVE, AND THE WELDER SHALL PERFORM THIS TASK. SHOULD THE INSPECTOR DETERMINE THAT THE WELDER HAS DISCONTINUED PERFORMANCE OF THIS TASK, THE TASK SHALL BE RETURNED TO PERFORM UNTIL SUCH TIME AS THE INSPECTOR HAS RE-ESTABLISHED ADEQUATE ASSURANCE THAT THE WELDER WILL PERFORM THE INSPECTION TASKS LISTED.
8 | SPECIAL INSPECTION OF MECHANICAL POST INSTALLED ANCHORS SHALL BE IN STRICT CONFORMANCE WITH THE ICC REPORT AND MANUFACTURER'S INSTALLATION REQUIREMENTS. ANCHOR INSTALLERS SHALL BE QUALIFIED AS REQUIRED BY JURISDICTION REQUIREMENTS.
● | INSPECTION REPORTS SHALL IDENTIFY NAMES OF INSTALLERS.
● | SPECIAL INSPECTOR SHALL PROVIDE DOCUMENTATION AT THE END OF ANCHOR INSTALLATIONS STATING THAT THE ANCHORS WERE INSPECTED PER APPROVED ANCHOR EVALUATION REPORT.
9 | TESTING ABBREVIATIONS:
NDT - NON-DESTRUCTIVE TESTING
C.J.P. - COMPLETE JOINT PENETRATION
MT - MAGNETIC PARTICLE TESTING
RBS - REDUCED BEAM SECTION
10 | DOCUMENT (D): INDICATES CONTRACTOR AND SPECIAL INSPECTOR TO PROVIDE DOCUMENTATION IN ACCORDANCE WITH AISC 341.
CONTRACTOR RESPONSIBILITY:
EACH CONTRACTOR RESPONSIBLE FOR THE CONSTRUCTION OF THE MAIN WIND-OR SEISMIC-FORCE-RESISTING SYSTEM, DESIGNATED SEISMIC SYSTEM OR A WIND-OR SEISMIC-RESISTING COMPONENT LISTED THE TABLES SHALL SUBMIT A WRITTEN STATEMENT OF RESPONSIBILITY TO THE BUILDING OFFICIAL AND THE OWNER PRIOR TO THE COMMENCEMENT OF WORK ON THE SYSTEM OR COMPONENT. THE CONTRACTOR'S STATEMENT OF RESPONSIBILITY SHALL CONTAIN THE FOLLOWING:
ACKNOWLEDGEMENT OF AWARENESS OF THE SPECIAL REQUIREMENTS CONTAINED IN THE STATEMENT OF SPECIAL INSPECTIONS.
1. | ACKNOWLEDGEMENT THAT CONTROL WILL BE EXERCISED TO OBTAIN CONFORMANCE WITH THE CONSTRUCTION DOCUMENTS APPROVED BY THE BUILDING OFFICIAL.
2. | PROCEDURES FOR EXERCISING CONTROL WITHIN THE CONTRACTOR'S ORGANIZATION, THE METHOD AND FREQUENCY OF REPORTING AND DISTRIBUTION OF THE REPORTS.
3. | IDENTIFICATION AND QUALIFICATIONS OF THE PERSON(S) EXERCISING SUCH CONTROL AND THEIR POSITION(S) IN THE ORGANIZATION.
TESTING NOTES:
1. | CASTELLATED BEAM POST TESTING REQUIREMENTS: (A.) PROVIDE ULTRASONIC TESTING ON THE GREATER OF 20% OF ALL WELDS OR FOUR WEB POST WELDS AT EACH CASTELLATED BEAM. THIS SHALL INCLUDE THE FIRST WEB POST AT EACH END OF THE BEAM AS WELL AS A MINIMUM OF TWO ADDITIONAL WEB POST WELDS SELECTED AT RANDOM FROM THE INTERIOR OF EACH BEAM SPAN. ULTRASONIC TESTING SHALL BE DONE IN ACCORDANCE WITH AWS D1.1 CRITERIA AND SHALL BE EVALUATED AGAINST ACCEPTANCE CRITERIA FOR STATICALLY LOADED STRUCTURES. (B.) FREQUENCY OF ULTRASONIC TESTING MAY BE REDUCED TO TWO MINIMUM WEB POSTS AT EACH BEAM ONCE A MINIMUM OF TEN BEAMS HAVE BEEN TESTED WITH OUT REJECTABLE FLAWS. TESTS SHALL INCLUDE ONE OF THE END WEB POSTS AND ONE POST SELECTED AT RANDOM ON EACH SUBSEQUENT BEAM. (C.) WHERE REJECTABLE FLAWS ARE ENCOUNTERED, THEY SHALL BE EVALUATED BY THE CELLULAR BEAM DESIGNER FOR DETERMINATION OF ANY NECESSARY REPAIRS, SUBJECT TO REVIEW AND APPROVAL BY THE ENGINEER OF RECORD. (D.) WHERE REJECTABLE FLAWS ARE DETECTED AND REPAIRS ARE REQUIRED PER ITEM (C.) ABOVE, 100% OF ALL WEB POST WELDS FOR THAT PARTICULAR BEAM SHALL BE TESTED. AND SAMPLING FREQUENCY FOR SUBSEQUENT BEAMS SHALL REVERT TO THE REQUIREMENTS STATED IN ITEM (A.) UNTIL AN ACCEPTABLE PASS RATE CAN AGAIN BE ESTABLISHED AS NOTED IN ITEM (B.)