Table 5 addresses code minimum testing requirements. It is the responsibility of the registered design professional to ensure testing types and extents are adequate. This section also lists some tests that are not specifically required by the 2014 OSSC but are customary; these items will be so described on an item-by-item basis.

# Soil (Table 1705.6, 1705.7 and 1705.8)

Soil evaluation requires both laboratory testing to determine Proctor values and field testing to determine in-place density. The responsible design professional should specify acceptance criteria including ASTM designation for maximum density testing method, percent compaction required and sampling intervals horizontally and vertically.

Tension anchors are generally subjected to performance tests and proof load tests. The responsible design professional should stipulate acceptance criteria and sampling intervals required.

# Concrete (Table 1705.3)

The 2012 IBC specifies minimum test frequencies, which are less than the test frequencies typically specified by most structural engineers. Consequently, engineers must exercise judgment here in order to balance structural needs against code minimums.

Concrete – Shotcrete (Table 1705.3)

When required by the Building Official, preconstruction tests per IBC 2012 Part 1910.5 will be needed. IBC 2012 Part 1910.10 requires strength testing of production shotcrete from in-place work or from test panels. A significant change from the UBC is that the IBC 2012 no longer specifies post-production core sampling from the completed work for visual evaluation of completed work. This may be an oversight but the engineer should specify what, if any, post-production testing is required.

Masonry (1705.4)

Testing requirements for masonry other than for seismic resistance depend upon the design method utilized. The 2014 OSSC provides for determination of masonry compressive strength (f’m) by the “unit strength method” or the “prism test method”.

For engineered masonry in non-essential facilities, verification of f’m is required, and at the discretion of the registered design professional and building official, verification of f’m can be with the first job site grouting. When the unit strength method is utilized no testing is required provided the strength of the masonry units and grout is confirmed by submitted test reports and the mortar type conforms to IBC Table 2105.2.2.1.1 for clay masonry units or 2105.2.2.1.2 for concrete masonry units. When the prism test method is utilized a set of three masonry prisms shall be constructed and tested in accordance with ASTM C-1314.

For engineered masonry in essential facilities, verification of f’m is required prior to construction and during construction. At the discretion of the registered design professional and building official, verification of f’m can be with the first job site grouting. When the unit strength method is utilized, Risk Category IV only requires three test prisms during construction for each 5,000 square feet of wall area. If the masonry compressive strength is greater than f’m = 1500 psi, the engineer may wish to also test unit strength during construction. Mortar type shall be verified. Mortar and grout proportions shall be verified.

When the prism test method is used for partially grouted masonry construction, construct and test both fully grouted and ungrouted masonry prisms. Test prisms at the specified age.

# Steel

The 2012 IBC, section 1705.12.2 states that testing for structural steel shall be in accordance with the quality assurance requirements of AISC 341 except for structures assigned to Seismic Design Category C and not specifically detailed for seismic resistance (R=3 or less) excluding cantilever column systems. AISC 341 Chapter J states that nondestructive testing (NDT) of steel construction is required for structural steel subject to tensile loading which is part of the seismic force resisting system (SFRS).  NDT requirements for applications other than seismic resistance are not specifically addressed in the IBC. However, they are addressed in AISC 360, section N which the IBC references. Section N5.5b states that CJP groove welds subject to transversely applied tension loading in butt, T, and corner joints in materials 5/16 in. thick and greater shall be subject to NDT for structures in occupancy category III and IV per ASCE 7. Structures in category II shall have NDT for 10% of CJP groove welds with transversely applied tension loads as previously stated.

AISC 341 chapter J7 states that inspections for high-strength bolts shall meet the requirements as stated in the AISC 360 specification section N5.6. Section N5.6 does not differentiate between requirements for seismically and non-seismically loaded structures. However, AISC 341 recommends that bolts which are part of the SFRS shall be considered for higher levels of observation.

# Sprayed Fire-Resistant Materials and Intumescent Fire-Resistive Coatings

# The 2014 OSSC does not specifically require testing of mastic and intumescent fire resistive coatings. AWCI Technical Manual 12B covering to Thin Film Intumescent Fire Resistive Materials (TFIFRM) is a recognized standard for reference.

# Smoke Control Systems

# These types of tests require very specialized personnel expertise along with specialized equipment. The specifier should understand that this is not a standard item for most special inspectors and that additional consideration should be given to these tests in terms of personnel qualifications and available equipment.

Exterior Insulation and Finish Systems, Water-Resistive Barrier Coating

Special inspection is required for the water-resistive barrier coating.