## Table 1
TABLE 1
REQUIRED GEOTECHNICAL SPECIAL INSPECTIONS
SYSTEM or MATERIAL | INSPECTION |  |  |  | REMARKS
| IBC CODE REFERENCE | CODE or STANDARD REFERENCE | FREQUENCY
|  |  | Continuous | Periodic
SOILS
GEOTECHNICAL INVESTIGATIONS | TABLE 1705.6 1803 |  |  |  | GEOTECHNICAL INVESTIGATION SHALL INCLUDE ITEMS OF SPECIAL INSPECTION AND TESTING AS NOTED IN TABLE 5 OF THE GUIDELINES
VERIFY MATERIALS BELOW SHALLOW FOUNDATIONS ARE ADEQUATE TO ACHIEVE THE DESIGN BEARING CAPACITY | TABLE 1705.6 |  |  | X (a) | BY THE GEOTECHNICAL ENGINEER
VERIFY EXCAVATIONS ARE EXTENDED TO PROPER DEPTH AND HAVE REACHED PROPER MATERIAL | TABLE 1705.6 |  |  | X
PERFORM CLASSIFICATION AND TESTING OF COMPACTED FILL MATERIALS | TABLE 1705.6 1803.5.1 |  |  | X | TESTING OF COMPACTED FILL MATERIALS (SEE TABLE 5)
VERIFY USE OF PROPER MATERIALS, DENSITIES AND LIFT THICKNESSES DURING PLACEMENT AND COMPACTION OF COMPACTED FILL | TABLE 1705.6 |  | X |  | BY THE GEOTECHNICAL ENGINEER
PRIOR TO PLACEMENT OF COMPACTED FILL, OBSERVE SUBGRADE AND VERIFY THAT SITE HAS BEEN PREPARED PROPERLY. | TABLE 1705.6 |  |  | X
DRIVEN DEEP FOUNDATION ELEMENTS
VERIFY ELEMENT MATERIALS, SIZES AND LENGTHS COMPLY WITH THE REQUIREMENTS | TABLE 1705.7 |  | X |  | BY THE GEOTECHNICAL ENGINEER
DETERMINE CAPACITIES OF TEST ELEMENTS AND CONDUCT ADDITIONAL LOAD TESTS, AS REQUIRED | TABLE 1705.7 |  | X |  | OBSERVATION BY GEOTECHNICAL ENGINEER
OBSERVE DRIVING OPERATIONS AND MAINTAIN COMPLETE AND ACCURATE RECORDS FOR EACH ELEMENT | TABLE 1705.7 |  | X
VERIFY PLACEMENT LOCATIONS AND PLUMBNESS, CONFIRM TYPE AND SIZE OF HAMMER, RECORD NUMBER OF BLOWS PER FOOT OF PENETRATION, DETERMINE REQUIRED PENETRATIONS TO ACHIEVE DESIGN CAPACITY, RECORD TIP AND BUTT ELEVATIONS AND DOCUMENT AND DAMAGE TO FOUNDATION ELEMENT | TABLE 1705.7 |  | X
FOR STEEL ELEMENTS, PERFORM ADDITIONAL INSPECTIONS IN ACCORDANCE WITH SECTION 1705.2 | TABLE 1705.7
FOR CONCRETE ELEMENTS AND CONCRETE-FILLED ELEMENTS, PERFORM ADDITIONAL INSPECTIONS IN ACCORDANCE WITH SECTION 1705.3 | TABLE 1705.7
FOR SPECIALTY ELEMENTS, PERFORM ADDITIONAL INSPECTIONS AS DETERMINED BY THE REGISTERED DESIGN PROFESSIONAL IN RESPONSIBLE CHARGE | TABLE 1705.7
CAST-IN-PLACE DEEP FOUNDATION ELEMENTS
DRILLING AND TESTING | 1705.8 | GEOTECHNICAL REPORT | X |  | BY THE GEOTECHNICAL ENGINEER
OBSERVE DRILLING OPERATIONS AND MAINTAIN COMPLETE AND ACCURATE RECORDS FOR EACH ELEMENT | TABLE 1705.8 |  | X
VERIFY PLACEMENT LOCATIONS AND PLUMBNESS, CONFIRM ELEMENT DIAMETERS, BELL DIAMETERS (IF APPLICABLE), LENGTHS, EMBEDMENT INTO BEDROCK (IF APPLICABLE) AND ADEQUATE END-BEARING STRATA CAPACITY. RECORD CONCRETE OR GROUT VOLUMES. | TABLE 1705.8 |  | X
FOR CONCRETE ELEMENTS, PERFORM ADDITIONAL INSPECTIONS IN ACCORDANCE WITH SECTION 1705.3 | TABLE 1705.8
HELICAL PILE FOUNDATIONS
INSTALLATION | 1705.9 | GEOTECHNICAL, RESEARCH AND/OR REPORT AND ICC EVALUATION REPORTS | X |  | BY THE GEOTECHNICAL ENGINEER SPECIAL INSPECTIONS APPLY TO VERIFYING MANUFACTURER'S CERTIFICATION OF INSTALLERS, HELICAL ANCHOR AND BRACKET PRODUCT NAME, TYPES, INSTALLATION EQUIPMENT USED, FINAL TORQUE, PILE DIMENSIONS, EMBEDMENT DEPTH AND TIP EVALUATION
MECHANICALLY STABILIZED EARTH (MSE) RETAINING WALLS
INSTALLATION | 1707.1 | GEOTECHNICAL RESEARCH AND/OR REPORT AND ICC EVALUATION REPORTS | X |  | BY THE GEOTECHNICAL ENGINEER SPECIAL INSPECTIONS APPLY TO MODULAR UNIT PRODUCT NAME, TYPE, AND DIMENSIONS, FOUNDATION PREPARATION, MODULAR UNIT PLACEMENT, INCLUDING ALIGNMENT AND INCLINATION, GEOSYNTHETIC REINFORCEMENT PRODUCT NAME, TYPE, AND PLACEMENT, BACKFILL PLACEMENT AND COMPACTION, AND DRAINAGE PROVISIONS
TENSION ANCHORS
INSTALLATION | 1707.1 | GEOTECHNICAL REPORT | X |  | BY THE GEOTECHNICAL ENGINEER SPECIAL INSPECTIONS APPLY TO TENDON TYPE AND SIZE, CORROSION PROTECTION, DEPTH OF EMBEDMENT, BONDED LENGTH, TYPE OF GROUT USED, AND RECORD OF PRESTRESS
STRESSING
STONE COLUMNS
INSTALLATION | 1707.1 | GEOTECHNICAL RESEARCH AND/OR REPORT AND ICC EVALUATION REPORTS | X |  | BY THE GEOTECHNICAL ENGINEER SPECIAL INSPECTIONS APPLY TO HOLE SIZE AND DEPTH, VERIFICATION OF AGGREGATE MATERIAL, NUMBER AND LIFTS OF AGGREGATE, INSTALLATION RAMMER ENERGY, AND TOP OF PIER ELEVATION

## Table 2
TABLE 2
REQUIRED STRUCTURAL SPECIAL INSPECTIONS
SYSTEM or MATERIAL | INSPECTION |  |  |  | REMARKS
| IBC CODE REFERENCE | CODE or STANDARD REFERENCE | FREQUENCY
|  |  | Continuous | Periodic
FABRICATORS
FABRICATORS | 1704.2.5 |  |  | X | SPECIAL INSPECTION IS REQUIRED FOR STRUCTURAL LOAD-BEARING MEMBERS AND ASSEMBLIES FABRICATED ON THE PREMISES OF A FABRICATOR'S SHOP.
| 1704.2.5.1 |  |  |  | THE SPECIAL INSPECTOR SHALL VERIFY THAT THE FABRICATOR MAINTAINS DETAILED FABRICATION AND QUALITY CONTROL PROCEDURES AND SHALL REVIEW FOR COMPLETENESS AND ADEQUACY RELATIVE TO THE CODE REQUIREMENT.
| 1704.2.5.2 |  |  |  | SPECIAL INSPECTIONS REQUIRED BY SECTION 1705 ARE NOT REQUIRED WHERE THE WORK IS DONE ON THE PREMISES OF A FABRICATOR REGISTERED AND APPROVED TO PERFORM SUCH WORK WITHOUT SPECIAL INSPECTION. APPROVAL SHALL BE BASED UPON REVIEW OF THE FABRICATOR'S WRITTEN PROCEDURAL AND QUALITY CONTROL MANUALS AND PERIODIC AUDITING OF FABRICATION PRACTICES BY A NATIONALLY RECOGNIZED ACCREDITING AUTHORITY. AT COMPLETION OF FABRICATION, THE APPROVED FABRICATOR SHALL SUBMIT A CERTIFICATE OF COMPLIANCE TO THE BUILDING OFFICIAL STATING THAT THE WORK WAS PERFORMED IN ACCORDANCE WITH THE APPROVED CONSTRUCTION DOCUMENTS.
CONCRETE
INSPECTION OF ANCHORS INSTALLED IN HARDENED CONCRETE | 1909.1 TABLE 1705.3 | ACI 318: 3.8.6, 8.1.3, 21.1.8 |  | X (a) | SPECIAL INSPECTIONS APPLY TO ANCHOR PRODUCT NAME, TYPE, AND DIMENSIONS, HOLE DIMENSIONS, COMPLIANCE WITH DRILL BIT REQUIREMENTS, CLEANLINESS OF THE HOLE AND ANCHOR, ADHESIVE EXPIRATION DATE, ANCHOR/ADHESIVE INSTALLATION, ANCHOR EMBEDMENT, AND TIGHTENING TORQUE
REINFORCING STEEL AND PRESTRESSING TENDON PLACEMENT | 1705.3 1910.4 1901.3.2 | ACI 318: 3.5 ACI 318: 7.1-7.7 |  | X | TOLERANCES AND REINFORCING PLACEMENT PER ACI 7.5; SPACING LIMITS FOR REINFORCING ACI 7.6 PROTECTION OF REINFORCEMENT PER ACI 7.7
WELDING REINFORCING STEEL | 1705.2.2.1.2 1903.1 | ACI 318: 3.5.2 AWS D1.4 | X |  | REFER TO STEEL FOR WELDING REQUIREMENTS TABLE 1705.2.2, ITEM 2b
1) VERIFICATION OF WELDABILITY OF REINFORCING STEEL OTHER THAN ASTM A 706 | TABLE 1705.2.2 | AWS D1.4 ACI 318: SECTION 3.5.2 |  | X
2) REINFORCING STEEL RESISTING FLEXURAL AND AXIAL FORCES IN INTERMEDIATE AND SPECIAL MOMENT FRAMES, AND BOUNDARY ELEMENTS OF SPECIAL STRUCTURAL WALLS OF CONCRETE AND SHEAR REINFORCEMENT | TABLE 1705.2.2 | AWS D1.4 ACI 318: SECTION 3.5.2 | X (b)
3) SHEAR REINFORCEMENT | TABLE 1705.2.2 | AWS D1.4 ACI 318: SECTION 3.5.2 | X
4) OTHER REINFORCING STEEL | TABLE 1705.2.2 | AWS D1.4 ACI 318: SECTION 3.5.2 |  | X
PLACEMENT OF BOLTS INSTALLED IN CONCRETE WHERE ALLOWABLE LOADS HAVE BEEN INCREASED OR WHERE STRENGTH DESIGN IS USED | TABLE 1705.3 1908.5 1909.1 | ACI 318: 1.3.2.C ACI 318: 8.1.3 ACI 318: 21.1.8 ACI 318 - APPENDIX D |  | X | ALL BOLTS VISUALLY INSPECTED
VERIFYING USE OF REQUIRED MIX DESIGN(S) | TABLE 1705.3 1904 1904.2 1910.2 1910.3 | ACI 318: CHAPTER 4 ACI 318: 5.2-5.4 |  | X
CONCRETE PLACEMENT | TABLE 1705.3 | ACI 318: 1.3.2.D ACI 318: 5.9 - 5.10 | X
SHOTCRETE PLACEMENT | TABLE 1705.3 1910.6-8 |  | X
CONCRETE PLACEMENT AT COMPOSITE SLABS |  | ASCE 9, CHAPTER 3 | X
CONCRETE/SHOTCRETE CURING | TABLE 1705.3 1910.9.1-3 | ACI 318: 5.11-5.13 |  | X (a)
VERIFICATION OF IN-SITU CONCRETE STRENGTH PRIOR TO STRESSING OF TENDONS IN POST-TENSIONED CONCRETE | TABLE 1705.3 1901.3.9 | ACI 318: 6.2 |  | X (a)
STRESSING OF TENDONS IN POST-TENSIONED CONCRETE | TABLE 1705.3 1901.3.10 | ACI 318: 18.20.1 | X
INSPECTION OF PRESTRESSED CONCRETE:
a. APPLICATION OF PRESTRESSING FORCES | TABLE 1705.3 | ACI 318: 18.20 | X
b. GROUTING OF BONDED PRESTRESSING TENDONS IN THE SEISMIC-FORCE-RESISTING SYSTEM | TABLE 1705.3 | ACI 318: 18.18.4 | X
ERECTION OF PRECAST MEMBERS | TABLE 1705.3 | ACI 318: CHAPTER 16 |  | X (a) | ALL CONNECTIONS VISUALLY INSPECTED REFER TO ANCHOR BOLT WELDING REQUIREMENTS AND STRUCTURAL INTEGRITY PROVISIONS
VERIFICATION OF IN-SITU CONCRETE PRIOR TO REMOVAL OF FORMS AND SHORES FROM ELEVATED BEAMS AND STRUCTURAL SLABS | TABLE 1705.3 | ACI 318: 6.2 |  | X (a)
VERIFICATION OF FORMWORK | TABLE 1705.3 | ACI 318: 6.1.1 |  | X (a) | SPECIAL INSPECTIONS APPLY TO SHAPE, LOCATION AND DIMENSIONS OF THE CONCRETE MEMBER BEING FORMED
MASONRY
EMPIRICALLY DESIGNED MASONRY, GLASS UNIT MASONRY, AND MASONRY VENEER IN RISK CATEGORY IV | SEC. 1705.4.1 | IBC |  | X | TABLE 1.19.2 LEVEL B QUALITY ASSURANCE MSJC
VERTICAL MASONRY FOUNDATION ELEMENTS | SEC 1705.4.2 | IBC | X | X | AS REQUIRED PER RISK CATEGORY
MASONRY LEVEL A
Table 1.19.1 – LEVEL A QUALITY ASSURANCE
TESTS
NONE
INSPECTION
VERIFY COMPLIANCE WITH THE APPROVED SUBMITTALS
MASONRY LEVEL B
TABLE 1.19.2 - LEVEL B QUALITY ASSURANCE
VERIFICATION OF SLUMP FLOW AND VISUAL STABILITY INDEX (VSI) AS DELIVERED TO THE PROJECT SITE IN ACCORDANCE WITH SPECIFICATION ARTICLE 1.5 B.1.b.3 FOR SELF-CONSOLIDATING GROUT
VERIFICATION OF F'M AND F'AAC IN ACCORDANCE WITH SPECIFICATION ARTICLE 1.4 B PRIOR TO CONSTRUCTION, EXCEPT WHERE SPECIFICALLY EXEMPTED BY THIS CODE
INSPECTION
INSPECTION TASK | REFERENCE CODE OR STANDARD FOR CRITERIA |  | FREQUENCY (a) |  | REMARKS
| TMS 402/ ACI 530/ ASCE 5 | TMS 602/ ACI 530.1/ ASCE 6
|  |  | Continuous | Periodic
1. VERIFY COMPLIANCE WITH THE APPROVED SUBMITTALS |  | Art. 1.5 |  | X
2. AS MASONRY CONSTRUCTION BEGINS, VERIFY THAT THE FOLLOWING ARE IN COMPLIANCE:
a. PROPORTIONS OF SITE-PREPARED MORTAR |  | Art. 2.1, 2.6 A |  | X
b. CONSTRUCTION OF MORTAR JOINTS |  | Art. 3.3 B |  | X
c. GRADE AND SIZE OF PRESTRESSING TENDONS AND ANCHORAGES |  | Art. 2.4 B, 2.4 H |  | X
d. LOCATION OF REINFORCEMENT, CONNECTORS, AND PRESTRESSING TENDONS AND ANCHORAGES |  | Art. 3.4, 3.6 A |  | X
e. PRESTRESSING TECHNIQUE |  | Art. 3.6 B |  | X
f. PROPERTIES OF THIN-BED MORTAR FOR AAC MASONRY |  |  | X(b) | X(c)
3. PRIOR TO GROUTING, VERIFY THAT THE FOLLOWING ARE IN COMPLIANCE: |  |  |  | X
a. GROUT SPACE |  | Art. 3.2 D, 3.2 F
b. GRADE, TYPE, AND SIZE OF REINFORCEMENT AND ANCHOR BOLTS, AND PRESTRESSING TENDONS AND ANCHORAGES | Sec. 1.16 | Art. 2.4, 3.4 |  | X
c. PLACEMENT OF REINFORCEMENT, CONNECTORS, AND PRESTRESSING TENDONS AND ANCHORAGES | Sec. 1.16 | Art. 3.2 E, 3.4, 3.6 A |  | X
d. PROPORTIONS OF SITE-PREPARED GROUT AND PRESTRESSING GROUT FOR BONDED TENDONS |  | Art. 2.6 B, 2.4 G.1.b |  | X
e. CONSTRUCTION MORTAR JOINTS |  | Art. 3.3 B |  | X
4. VERIFY DURING CONSTRUCTION:
a. SIZE AND LOCATION OF STRUCTURAL ELEMENTS |  | Art. 3.3 F |  | X
b. TYPE, SIZE, AND LOCATION OF ANCHORS, INCLUDING OTHER DETAILS OF ANCHORAGE OF MASONRY TO STRUCTURAL MEMBERS, FRAMES, OR OTHER CONSTRUCTION | Sec. 1.16.4.3, 1.17.1 |  |  | X
c. WELDING OF REINFORCEMENT | Sec. 2.1.7.7.2, 3.3.3.4 (c), 8.3.3.4 (b) |  | X
d. PREPARATION, CONSTRUCTION, AND PROTECTION OF MASONRY DURING COLD WEATHER (TEMPERATURE BELOW 40°F (4.4°C)) OR HOT WEATHER (TEMPERATURE ABOVE 90°F (32.2°C)) |  | Art. 1.8 C, 1.8 D |  | X
e. APPLICATION AND MEASUREMENT OF PRESTRESSING FORCE | Art. 3.6 B |  | X
f. PLACEMENT OF GROUT AND PRESTRESSING GROUT FOR BONDED TENDONS IS IN COMPLIANCE | Art. 3.5, 3.6 C |  | X |  | Art. 3.5, 3.6 C
g. PLACEMENT OF AAC MASONRY UNITS AND CONSTRUCTION OF THIN-BED MORTAR JOINTS | Art. 3.3 B.8 |  | X(b) | X(c)
5. OBSERVE PREPARATION OF GROUT SPECIMENS, MORTAR SPECIMENS, AND/OR PRISMS |  | Art. 1.4 B.2.a.3, 1.4 B.2.b.3, 1.4 B.2.c.3, 1.4 B.3, 1.4 B.4 |  | X
(a) Frequency refers to the frequency of inspection, which may be continuous during the task listed or periodically during the listed task, as defined in the table.
(b) Required for the first 5000 square feet (465 square meters) of AAC masonry.
(c) Required after the first 5000 square feet (465 square meters) of AAC masonry.
MASONRY LEVEL C
TABLE 1.19.3 - LEVEL C QUALITY ASSURANCE
TESTS
VERIFICATION OF f’m AND f’AAC IN ACCORDANCE WITH SPECIFICATION ARTICLE 1.4 B PRIOR TO CONSTRUCTION AND FOR EVERY 5,000 SQ. FT (465 SQ. M) DURING CONSTRUCTION
VERIFICATION OF PROPORTIONS OF MATERIALS IN PREMIXED OR PREBLENDED MORTAR, PRESTRESSING GROUT, AND GROUT OTHER THAN SELF-CONSOLIDATING GROUT, AS DELIVERED TO THE PROJECT SITE
VERIFICATION OF SLUMP FLOW AND VISUAL STABILITY INDEX (VSI) AS DELIVERED TO THE PROJECT SITE IN ACCORDANCE WITH ARTICLE 1.5 B.1.b.3 FOR SELF-CONSOLIDATING GROUT
INSPECTION
INSPECTION TASK | REFERENCE CODE OR STANDARD FOR CRITERIA |  | FREQUENCY (a) |  | REMARKS
| TMS 402/ ACI 530/ ASCE 5 | TMS 602/ ACI 530.1/ ASCE 6
|  |  | Continuous | Periodic
1. VERIFY COMPLIANCE WITH THE APPROVED SUBMITTALS |  | Art. 1.5 |  | X
2. VERIFY THAT THE FOLLOWING ARE IN COMPLIANCE:
a. PROPORTIONS OF SITE-MIXED MORTAR, GROUT AND PRESTRESSING GROUT FOR BONDED TENDONS |  | Art. 2.1, 2.6 A, 2.6 B, 2.6 C, 2.4 G.1.b |  | X
b. GRADE, TYPE, AND SIZE OF REINFORCEMENT AND ANCHOR BOLTS, AND PRESTRESSING TENDONS AND ANCHORAGES | Sec. 1.16 | Art. 2.4, 3.4 |  | X
c. PLACEMENT OF MASONRY UNITS AND CONSTRUCTION OF MORTAR JOINTS |  | Art. 3.3 B |  | X
d. PLACEMENT OF REINFORCEMENT, CONNECTORS, AND PRESTRESSING TENDONS AND ANCHORAGES | Sec. 1.16 | Art. 3.2 E, 3.4, 3.6 A | X
e. GROUT SPACE PRIOR TO GROUTING |  | Art. 3.2 D, 3.2 F | X
f. PLACEMENT OF GROUT AND PRESTRESSING GROUT FOR BONDED TENDONS |  | Art. 3.5, 3.6 C | X
g. SIZE AND LOCATION OF STRUCTURAL ELEMENTS |  | Art. 3.3 F |  | X
h. TYPE, SIZE, AND LOCATION OF ANCHORS INCLUDING OTHER DETAILS OF ANCHORAGE OF MASONRY TO STRUCTURAL MEMBERS, FRAMES, OR OTHER CONSTRUCTION | Sec. 1.16.4.3, 1.17.1 |  | X
i. WELDING OF REINFORCEMENT | 1705.2.2.1.2 Sec. 2.1.8.7.2, 3.3.3.4 (c), 8.3.3.4 (b) |  | X
j. PREPARATION, CONSTRUCTION, AND PROTECTION OF MASONRY DURING COLD WEATHER (TEMPERATURE BELOW 40°F (4.4°C)) OR HOT WEATHER (TEMPERATURE ABOVE 90°F (32.2°C)) |  | Art. 1.8 C, 1.8 D |  | X
k. APPLICATION AND MEASUREMENT OF PRESTRESSING FORCE |  | Art. 3.6 B | X
l. PLACEMENT OF AAC MASONRY UNITS AND CONSTRUCTION OF THIN-BED MORTAR JOINTS |  | Art. 3.3 B.8 | X
m. PROPERTIES OF THIN-BED MORTAR FOR AAC MASONRY |  | Art. 21.C.1 | X
3. OBSERVE PREPARATION OF GROUT SPECIMENS, MORTAR SPECIMENS, AND/OR PRISMS |  | Art. 1.4 B.2.a.3, 1.4 B.2.b.3, 1.4 B.2.c.3, 1.4 B.3, 1.4 B.4 | X
STEEL
FABRICATION OF STRUCTURAL ELEMENTS | 1704.2.5.2 | AISC 360 N2 |  | X | REFER TO INSPECTION OF FABRICATOR REQUIREMENTS APPROVAL BASED ON NATIONALLY RECOGNIZED ACCREDITING AUTHORITY
MATERIAL VERIFICATION OF HIGH-STRENGTH BOLTS, NUTS, AND WASHERS |  | AISC 360 A3.3 AISC 360 N 3.2 ASTM STANDARDS SPECIFIED IN CONSTRUCTION DOCUMENTS RCSC 2.1 |  | X | MANUFACTURER'S CERTIFIED TEST REPORTS
SNUG-TIGHT JOINT HIGH-STRENGTH BOLT INSTALLATION | 1705.2.1.1 | RCSC SPECIFICATION FOR STRUCTURAL JOINTS USING ASTM A325 OR A490 BOLTS SECTION 9 AISC 360, SECTION M2.5 |  | X | ALL CONNECTIONS INSPECTED AND VERIFIED SNUG
PRETENSIONED AND SLIP-CRITICAL JOINT HIGH-STRENGTH BOLT INSTALLATION USING TURN-OF-THE-NUT METHOD WITH MATCH MARKING, TWIST-OFF BOLT OR DIRECT TENSION INDICATOR METHOD | 1705.2.1.1 |  |  | X | ALL CONNECTIONS INSPECTED. CONNECTIONS USING DIRECT TENSION INDICATORS, ALL BOLTS SHALL BE INSPECTED AFTER SNUGGING AND AFTER PRETENSIONING
PRETENSIONED AND SLIP-CRITICAL JOINT HIGH-STRENGTH BOLT INSTALLATION USING TURN-OF-THE-NUT METHOD WITHOUT MATCH MARKING OR CALIBRATED WRENCH METHOD | 1705.2.1.1 |  | X |  | ALL CONNECTIONS INSPECTED
MATERIAL VERIFICATION OF STRUCTURAL STEEL | 1705.2.1 2203.1 TABLE 1705.2 | ASTM A6 ASTM STANDARDS SPECIFIED IN CONSTRUCTION DOCUMENTS AISC 360 N3.2 AISC 360 A3.1 AISC 360 M5.5 |  | X | CERTIFIED MILL TEST REPORTS
FOR OTHER STEEL, IDENTIFICATION MARKINGS TO CONFORM TO ASTM STANDARDS SPECIFIED IN THE APPROVED CONSTRUCTION DOCUMENTS | TABLE 1705.2 | APPLICABLE ASTM MATERIAL STANDARDS |  | X | MANUFACTURER'S CERTIFIED TEST REPORTS
MATERIAL VERIFICATION OF WELD FILLER METALS | TABLE 1705.2 | AISC 360 N3.2 AISC 360 A3.5 APPLICABLE AWS A5 DOCUMENTS |  | X | MANUFACTURER'S CERTIFICATE OF COMPLIANCE
COMPLETE AND PARTIAL JOINT PENETRATION GROOVE WELDS | TABLE 1705.2 | AWS D1.1 SECTION 6 | X |  | ALL WELDS VISUALLY INSPECTED PER AWS D1.1 6.9
MULTIPASS FILLET WELDS | TABLE 1705.2 | AWS D1.1 SECTION 6 | X |  | ALL WELDS VISUALLY INSPECTED PER AWS D1.1 6.9
SINGLE PASS FILLET WELDS GREATER THAN 5/16" | TABLE 1705.2 | AWS D1.1 SECTION 6 | X |  | ALL WELDS VISUALLY INSPECTED PER AWS D1.1 6.9
PLUG AND SLOT WELDS | TABLE 1705.2 | AWS D1.1 SECTION 6 | X |  | ALL WELDS VISUALLY INSPECTED PER AWS D1.1 6.9
SINGLE PASS FILLET WELDS LESS THAN OR EQUAL TO 5/16" | TABLE 1705.2 | AWS D1.1 SECTION 6 |  | X | ALL WELDS VISUALLY INSPECTED PER AWS D1.1 6.9
FLOOR AND ROOF DECK WELDS | TABLE 1705.2 | AWS D1.3 SECTION 7 |  | X | ALL WELDS INSPECTED PER AWS D1.3 7.1
MATERIAL VERIFICATION OF REINFORCING STEEL FOR WELDING | TABLE 1705.2 1705.2.2.1.2 | ACI 318: 3.5.2 AWS D1.4 |  | X | CERTIFIED MILL TEST REPORTS
WELDING REINFORCING STEEL IN MOMENT RESISTING FRAMES | TABLE 1705.2 1705.2.2.1.2 | ACI 318: 3.5.2 AWS D1.4 | X |  | ALL WELDS VISUALLY INSPECTED PER AWS D1.4 7.5
WELDING REINFORCING STEEL IN SHEAR WALL BOUNDARY ELEMENTS | TABLE 1705.2 1705.2.2.1.2 | ACI 318: 3.5.2 AWS D1.4 | X |  | ALL WELDS VISUALLY INSPECTED PER AWS D1.4.7.5
WELDING SHEAR REINFORCEMENT | TABLE 1705.2 1705.2.2.1.2 | ACI 318: 3.5.2 AWS D1.4 | X |  | ALL WELDS VISUALLY INSPECTED PER AWS D1.4.7.5
WELDING REINFORCING EXCEPT AS NOTED OTHERWISE | TABLE 1705.2 1705.2.2.1.2 | ACI 318: 3.5.2 AWS D1.4 |  | X
VERIFICATION OF FRAME JOINT DETAILS INCLUDING MEMBER AND COMPONENT LOCATIONS, BRACING, AND STIFFENERS | TABLE 1705.2 | AISC 360 N5.7 |  | X (a)
MATERIAL VERIFICATION OF ANCHOR BOLTS AND THREADED RODS |  | AISC 360 N3.2 AISC 360 A3.4 ASTM STANDARDS SPECIFIED IN CONSTRUCTION DOCUMENTS |  | X | MANUFACTURER'S CERTIFIED TEST REPORTS
VERIFYING USE OF PROPER WPS'S |  | AISC 360 N3.2 |  |  | COPY OF WELDING PROCEDURE SPECIFICATIONS
VERIFYING WELDER AND WELDING INSPECTOR QUALIFICATIONS | 1705.2.2.1 |  |  | X | COPY OF QUALIFICATION CARDS
INSTALLATION OF COMPOSITE SLAB DECKING | 1705.1.1 | ICC EVALUATION REPORT ASCE 9 CHAPTER 3 |  | X | SPECIAL INSPECTIONS APPLY TO DECKING TYPE, DEPTH, GAGE, AND FASTENING
INSTALLATION OF ROOF DECKING | 1705.1.1 | ICC EVALUATION REPORT |  | X | SPECIAL INSPECTIONS APPLY TO DECKING TYPE, DEPTH AND GAGE, POWER ACTUATED FASTENERS, SCREWS, PROPRIETARY SIDE SEAM ATTACHMENTS, BUTTON PUNCHES AND SHEAR CONNECTORS
WELDING STUDS EXCEPT AS NOTED OTHERWISE |  | AISC 360 N6 AWS D1.1 SECTION 7 | X |  | CONTINUOUS INSPECTION IS NOT REQUIRED WHEN WELDS INSTALLED WITH AN AUTOMATICALLY TIMED STUD WELDING MACHINE PER SECTION 7 OF AWS D1.1 (ONLY PERIODIC), 1705.2 (3) ALL WELDS VISUALLY INSPECTED PER AWS D1.1 7.8.1
WELDING STUDS IN STRUCTURAL DIAPHRAGMS |  |  |  | X
WELDING STAIR AND RAILING SYSTEMS | 1705.2 (2.5) | AWS D1.1 SECTION 6 |  | X | ALL WELDS VISUALLY INSPECTED PER AWS D1.1 6.9
PROPRIETARY MOMENT RESISTING FRAME CONNECTION SYSTEMS | 1705.1.1 | REFER TO WELDING AND HIGH STRENGTH BOLTING REQUIREMENTS (b)
STAINLESS STEEL
FABRICATION OF STAINLESS STEEL ELEMENTS | 1705.1.1 |  |  | X | REFER TO INSPECTION OF FABRICATOR REQUIREMENTS
MATERIAL VERIFICATION OF STAINLESS STEEL | 1705.1.1 |  |  | X | CERTIFIED MILL TEST REPORTS
MATERIAL VERIFICATION OF BOLTS | 1705.1.1 |  |  | X | MANUFACTURER'S CERTIFIED TEST REPORTS
MATERIAL VERIFICATION OF WELD FILLER METALS | 1705.1.1 | AWS D1.6 SECTION 6 |  | X | MANUFACTURER'S CERTIFIED TEST REPORTS
VERIFYING USE OF PROPER WPS'S |  |  |  | X | COPY OF WELDING PROCEDURE SPECIFICATIONS
VERIFYING WELDER QUALIFICATIONS |  |  |  | X | COPY OF QUALIFICATION CARDS
COMPLETE AND PARTIAL JOINT PENETRATION GROOVE WELDS |  |  | X |  | ALL WELDS VISUALLY INSPECTED PER AWS D1.6 6.28.1
MULTIPASS FILLET WELDS |  |  | X
SINGLE PASS FILLET WELDS |  |  |  | X
COLD-FORMED STEEL FRAMING
MATERIAL VERIFICATION OF WELD FILLER METALS |  | AWS D1.3 SECTION 7 |  | X | MANUFACTURER'S CERTIFIED TEST REPORTS
VERIFYING USE OF PROPER WPS'S |  |  |  | X | COPY OF WELDING PROCEDURE SPECIFICATIONS
COLD-FORMED STEEL ROOF AND FLOOR DECKS | 1705.2.2.1.1 | AWS D1.3 |  | X | WELDING INSPECTION AND INSPECTOR QUALIFICATION
VERIFYING WELDER AND WELDING INSPECTOR QUALIFICATIONS | 1705.2.2.1 |  |  | X | COPY OF QUALIFICATION CARDS
WELDED FRAMING CONNECTIONS | 1705.2.2.1 | AWS D1.3 SECTION 7 |  | X | ALL WELDS VISUALLY INSPECTED PER AWS D1.3 7.1
COLD-FORMED STEEL TRUSSES SPANNING 60 FEET OR GREATER | 1705.2.2.2 |  |  | X | VERIFY THAT THE TEMPORARY INSTALLATION RESTRAINT/BRACES AND THE PERMANENT INDIVIDUAL TRUSS MEMBER RESTRAINT/BRACING ARE INSTALLED IN ACCORDANCE WITH THE APPROVED TRUSS SUBMITTAL PACKAGE
INSPECTION OF ANCHORS INSTALLED IN HARDENED CONCRETE | 1908.5 TABLE 1705.3 | ICC EVALUATION REPORT |  | X
ALUMINUM
MATERIAL VERIFICATION OF STRUCTURAL ALUMINUM | 1705.1.1 |  |  | X | CERTIFIED MILL TEST REPORTS
MATERIAL VERIFICATION OF BOLTS |  |  |  | X | MANUFACTURER'S CERTIFIED TEST REPORTS
MATERIAL VERIFICATION OF WELD FILLER METALS |  | AWS D1.2 SECTION 5 |  | X | MANUFACTURER'S CERTIFIED TEST REPORTS
VERIFYING USE OF PROPER WPS'S |  |  |  | X | COPY OF WELDING PROCEDURE SPECIFICATIONS
VERIFYING WELDER QUALIFICATIONS |  |  |  | X | COPY OF QUALIFICATION CARDS
COMPLETE AND PARTIAL JOINT PENETRATION GROOVE WELDS |  |  | X |  | ALL WELDS VISUALLY INSPECTED PER AWS 1.2, 5.5
MULTIPASS FILLET WELDS |  |  | X
SINGLE PASS FILLET WELDS |  |  |  | X
WOOD
FABRICATION OF PREFABRICATED STRUCTURAL ELEMENTS | 1705.5 |  |  | X | REFER TO INSPECTION OF FABRICATOR REQUIREMENTS
1. FABRICATION OF HIGH-LOAD DIAPHRAGMS:
A. VERIFY STRUCTURAL PANEL GRADE AND THICKNESS | 1705.5.1 TABLE 2306.2 (2) |  |  | X
B. VERIFY NOMINAL SIZE OF FRAMING MEMBERS AT ADJOINING PANEL EDGES | 1705.5.1 TABLE 2306.2 (2) |  |  | X
C. VERIFY NAIL OR STAPLE DIAMETER AND LENGTH, NUMBER OF FASTENER LINES AND SPACING BETWEEN FASTENERS IN EACH LINE AND AT EDGE MARGINS | 1705.5.1 TABLE 2306.2 (2) |  |  | X
PREFABRICATED WOOD SHEAR PANELS | 1705.5 1704.2.5 | ICC EVALUATION REPORT |  | X | SPECIAL INSPECTIONS APPLY TO HOLDOWN ANCHOR SIZE AND PLACEMENT, INCLUDING EMBEDMENT LENGTH, SPACING, AND EDGE DISTANCE
METAL-PLATE-CONNECTED WOOD TRUSSES SPANNING 60 FEET OR GREATER | 1705.5.2 |  |  |  | VERIFY THAT TEMPORARY AND PERMANENT RESTRAINT/BRACING ARE INSTALLED IN ACCORDANCE WITH APPROVED TRUSS SUBMITTAL

## Table 3
TABLE 3
REQUIRED ARCHITECTURAL SPECIAL INSPECTIONS
SYSTEM or MATERIAL | INSPECTION |  |  |  | REMARKS
| IBC CODE REFERENCE | CODE or STANDARD REFERENCE | FREQUENCY
|  |  | Continuous | Periodic
SPRAYED FIRE-RESISTANT MATERIALS
CONDITIONS OF SUBSTRATE | 1705.13 | APPROVED CONSTRUCTION DOCUMENTS |  | X | SPECIAL INSPECTIONS APPLY TO CLEANLINESS AND TEMPERATURE OF SUBSTRATE AND THE ACCEPTABILITY OF PRIMED, PAINTED, OR ENCAPSULATED STEEL
APPLICATION |  | WRITTEN INSTRUCTION OF APPROVED MANUFACTURER |  | X | SPECIAL INSPECTIONS APPLY TO USE OF APPROVED MATERIAL VERIFICATION, MATERIAL EXPIRATION, HANDLING, STORAGE, MIXING, CONVEYANCE, METHOD OF APPLICATION, CURING, VENTILATION, THICKNESS, DENSITY, BOND STRENGTH AND CONDITION OF APPLICATION, AND PATCHING
MASTIC AND INTUMESCENT FIRE-RESISTIVE COATINGS
CONDITIONS OF SUBSTRATE | 1705.14 | APPROVED CONSTRUCTION DOCUMENTS |  | X | SPECIAL INSPECTIONS APPLY TO CLEANLINESS AND TEMPERATURE OF SUBSTRATE AND THE ACCEPTABILITY OF PRIMED, PAINTED, OR ENCAPSULATED STEEL
APPLICATION |  | AWCI TECHNICAL MANUAL 12-B |  | X | SPECIAL INSPECTIONS APPLY TO USE OF APPROVED MATERIAL VERIFICATION, MATERIAL EXPIRATION, HANDLING, STORAGE, MIXING, CONVEYANCE, METHOD OF APPLICATION, PROTECTION, CURING, VENTILATION, THICKNESS, VOIDS REPAIR, CONDITION OF APPLICATION, AND PATCHING
EXTERIOR INSULATION AND FINISH SYSTEMS
EIFS APPLICATION | 1705.15 | APPROVED CONSTRUCTION DOCUMENTS |  | X | ALL EIFS APPLICATIONS EXCEPT FOR APPLICATIONS OVER WATER-RESISTIVE BARRIERS WITH A MEANS OF DRAINING MOISTURE TO THE EXTERIOR OR OVER MASONRY OR CONCRETE WALLS
WATER-RESISTIVE BARRIER COATING APPLICATION | 1705.15.1 | APPROVED CONSTRUCTION DOCUMENTS |  | X | A WATER-RESISTIVE BARRIER COATING COMPLYING WITH ASTM E2570 REQUIRES SPECIAL INSPECTION OF THE WATER-RESISTIVE BARRIER COATING WHEN INSTALLED OVER A SHEATHING SUBSTRATE
MANUFACTURERS WRITTEN ASTM E2570 INSTRUCTIONS
SMOKE CONTROL SYSTEMS
INSTALLATION | 1705.17 | APPROVED CONSTRUCTION DOCUMENTS |  | X | LEAKAGE TESTING AND DEVICE LOCATION PRIOR TO CONCEALMENT PRESSURE DIFFERENCE TESTING, FLOW MEASUREMENTS AND DETECTION AND CONTROL VERIFICATION PRIOR TO OCCUPANCY SPECIAL INSPECTION AGENCIES FOR SMOKE CONTROL SHALL HAVE EXPERTISE IN FIRE PROTECTION ENGINEERING, MECHANICAL ENGINEERING AND CLARIFICATION AS AIR BALANCERS
FIRE-RESISTANT PENETRATIONS AND JOINTS
FIRE-RESISTANT PENETRATIONS AND JOINTS | 1705.16 714 715 | ASTM E2393 ASTM E2174 MANUFACTURERS TESTING AND LISTING INSTRUCTIONS |  | X | IN HIGH-RISE BUILDINGS OR IN BUILDINGS ASSIGNED TO RISK CATEGORY III OR IV, SPECIAL INSPECTIONS FOR THROUGH-PENETRATIONS, MEMBRANE PENETRATION FIRESTOPS, FIRE-RESISTANT JOINT SYSTEMS AND PERIMETER FIRE BARRIER SYSTEMS THAT ARE TESTED AND LISTED
RADON MITIGATION INSPECTION
WHERE RADON MITIGATION SYSTEMS ARE REQUIRED BY SECTION 1811 OF THIS CODE, SPECIAL INSPECTIONS SHALL BE PROVIDED PER THE METHODS AND FREQUENCY IN SECTION 1705.18 | 1705.18 |  |  | X

## Table 4
TABLE 4
REQUIRED INSPECTIONS for SPECIAL CASES
SYSTEM or MATERIAL | INSPECTION |  |  |  | REMARKS
| IBC CODE REFERENCE | CODE or STANDARD REFERENCE | FREQUENCY
|  |  | Continuous | Periodic
PRE-ENGINEERED STRUCTURES
FABRICATION AND ERECTION | 1705.1.1 |  | X (b) | X | REFER TO TABLE 2 OF THIS PLAN FOR FABRICATOR, WELDING, AND HIGH STRENGTH BOLTING SPECIAL INSPECTION REQUIREMENTS
WELDED STEEL TANKS
FABRICATION AND ERECTION | 1075.1.1 | AWWA/AWS D100 SECTION 11 API 650 5.3 API 620 SECTION 5 |  | X | ALL JOINTS VISUALLY INSPECTED
STAINLESS STEEL
STAINLESS STEEL | 1705.1.1 | AWS D1.6 SECTION 6 |  |  | STAINLESS STEEL IS NOT THE SAME AS STRUCTURAL STEEL AND IS NOT A STRUCTURAL MATERIAL SPECIFICALLY REFERENCED BY THE IBC. AWS D1.6 IS THE WELDING CODE APPLICABLE TO WELDED STAINLESS STEEL.

## Table 5
TABLE 5
REQUIRED TESTING for SPECIAL INSPECTIONS
SYSTEM or MATERIAL | TESTING |  |  |  | REMARKS
| IBC CODE REFERENCE | CODE or STANDARD REFERENCE | FREQUENCY
|  |  | Continuous | Periodic
GEOTECHNICAL
GEOTECHNICAL ENGINEER TO PERFORM TESTING OF COMPACTED FILL MATERIALS | 1803 |  |  |  | TESTING PER GEOTECHNICAL REPORT
FILL IN-PLACE DENSITY OR PREPARED SUBGRADE DENSITY | 1705.6 |  |  | X (a) | BY THE GEOTECHNICAL ENGINEER
MATERIAL VERIFICATION |  | VARIES; CLASSIFICATION AND TESTING OF CONTROLLED FILL MATERIALS |  | X (a) | BY THE GEOTECHNICAL ENGINEER
TENSION ANCHORS | 1705.6 |  | PERFORMANCE TEST FIRST (X) ANCHORS TO xxx% DL AND PROOF LOAD REMAINING ANCHORS TO xxx% DL |  | PER GEOTECHNICAL REPORT
CONCRETE
AT THE TIME FRESH CONCRETE IS SAMPLED TO FABRICATE SPECIMENS FOR STRENGTH TESTS, PERFORM SLUMP AND AIR CONTENT TESTS, AND DETERMINE THE TEMPERATURE OF THE CONCRETE | TABLE 1705.3 | ASTM C 172 ASTM C 31 ACI 318: 5.6, 5.8 | X |  | FABRICATE SPECIMENS AT TIME FRESH CONCRETE IS PLACED ONCE EACH DAY FOR A GIVEN CLASS OF CONCRETE, OR LESS THAN ONCE FOR EACH 150 YDS OF CONCRETE, OR LESS THAN ONCE FOR EACH 5,000 FT2 OF SURFACE AREA FOR SLABS/WALLS. ONCE EACH SHIFT FROM IN-PLACE WORK OR FROM TEST PANEL AND MINIMUM ONE SPECIMEN FOR EACH 50 CUBIC YARDS. "PRECONSTRUCTION TESTS AS REQUIRED PER THE BUILDING OFFICIAL."
CONCRETE STRENGTH | TABLE 1705.3 | ASTM C39 | X
CONCRETE SLUMP | TABLE 1705.3 | ASTM C143 | X
CONCRETE AIR CONTENT |  | ASTM C231 | X
CONCRETE TEMPERATURE |  | ASTM C1064 | X
SHOTCRETE STRENGTH | 1910.10 | ASTM C42 | X |  | IBC 1910.10: SPECIMENS SHALL BE TAKEN FROM THE IN-PLACE OR FROM TEST PANELS, AND SHALL BE TAKEN AT LEAST ONCE EACH SHIFT, BUT NOT LESS THAN ONE FOR EACH 50 CUBIC YARDS OF SHOTCRETE
MASONRY
UNIT STRENGTH METHOD | 2105.2.2.1 TABLE 2105.2.2.1.1 TABLE 2105.2.2.1.2 | ASTM C62 ASTM C216 ASTM C652 ASTM 1019 ASTM C55 ASTM C90 ASTM C1386 | TESTING EVERY 5,000 FT2 AT LEVEL C QUALITY ASSURANCE
PRISM TEST METHOD | 2105.2.2.2 | ASTM C1314 | TESTING EVERY 5,000 FT2 AT LEVEL C QUALITY ASSURANCE |  | THREE PRISMS PER TEST
COMPRESSIVE STRENGTH OF MORTAR |  | MSJC ASTM C270
COMPRESSIVE STRENGTH OF GROUT |  | MSJC ASTM C1019
TESTING PRISMS FROM CONSTRUCTED MASONRY | 2105.3 | MSJC TMS 602-11/ ACI 530.1-11/ ASCE 6-11/ ASTM C1314 | THREE MASONRY PRISMS FOR EACH 5000 SQ. FT.
STEEL
MAGNETIC PARTICLE (MT) AND ULTRASONIC (UT) TESTING OF WELDS | 1705.2.2 | MT - AWS D1.1 6.14.4 UT - AWS D1.1 6.13 & 6.14.3 | PER DRAWINGS
PRE-CONSTRUCTION TESTING OF WELDING STUDS | 1705.2.2 | AWS D1.1 7.7.1 | EACH SIZE AND TYPE OF STUD EACH SHIFT |  | THIS TESTING PERFORMED BY CONTRACTOR AND CONFIRMED BY SPECIAL INSPECTOR.
STUD APPLICATION QUALIFICATION | 1705.2.2 | AWS D1.1 7.6 | NON-PREQUALIFIED APPLICATIONS |  | THIS TESTING PERFORMED BY CONTRACTOR AND CONFIRMED BY SPECIAL INSPECTOR.
PRE-INSTALLATION VERIFICATION OF PRETENSIONED HIGH STRENGTH BOLTS | 1705.2.2 | RCSC SPECIFICATION FOR STRUCTURAL JOINTS USING ASTM A325 OR A490 BOLTS SECTION 7 | EACH COMBINATION OF DIAMETER, LENGTH, GRADE, AND LOT TO BE USED IN THE WORK
STAINLESS STEEL
ULTRASONIC (UT) TESTING OF WELDS | 1704.3.1 | UT-AWS D1.6 6.13 | PER DRAWINGS
ALUMINUM
LIQUID PENETRANT (PT) AND RADIOGRAPHIC (RT) TESTING OF WELDS |  | PT - AWS D1.2 5.7.5 RT - AWS D1.2 5.10 & 5.15 | PER DRAWINGS
WELDED STEEL TANKS
RADIOGRAPHIC TESTING (RT) OF WELDS |  | AWWA/AWS D100 11.5 & 11.6 API 650 6.1 API 620 5.15.1 | AT SHELL JOINTS - NUMBER AND SPACING PER THE STANDARD |  | SPECIAL INSPECTIONS APPLY TO REVIEW OF THE RADIOGRAPHS AND THE ASSOCIATED REPORT INTERPRETING THE RADIOGRAPHS
MASTIC & INTUMESCENT FIRE-RESISTIVE COATINGS
THICKNESS | 1705.14 | AWCI TECHNICAL MANUAL 12-B | EACH 10,000 SF OF COATED AREA EACH FLOOR LEVEL
SMOKE CONTROL SYSTEMS
LEAKAGE AND PRESSURE DIFFERENTIAL AND FLOW MEASUREMENT | 1705.17.1 |  | DETERMINED BY JURISDICTION
DETECTION AND CONTROL VERIFICATION |  |  | DETERMINED BY JURISDICTION
SPRAYED FIRE-RESISTANT MATERIALS
THICKNESS @ FLOOR, ROOF, AND WALL ASSEMBLIES | 1705.13.4 1705.13.4.1 1705.13.4.2 | ASTM E605 | NOT LESS THAN (4) MEASUREMENTS FOR EACH 1000 SF OF SPRAYED AREA EACH FLOOR LEVEL
THICKNESS @ STRUCTURAL MEMBERS | 1705.13.4 1705.13.4.1 1705.13.4.5 |  | THICKNESS DETERMINED FOR NOT LESS THAN 25% THE STRUCTURAL MEMBERS EACH FLOOR LEVEL
DENSITY @ FLOOR, ROOF, AND WALL ASSEMBLIES | 1705.13.5 |  | DETERMINED FROM EACH FLOOR, ROOF, AND WALL ASSEMBLY AT A RATE OF NOT LESS THAN ONE SAMPLE FOR EVERY 2500 SF IN EACH STORY
DENSITY @ BEAMS, GIRDERS, TRUSSES, AND COLUMNS | 1705.13.5 |  | DETERMINED FROM EACH TYPE OF STRUCTURAL MEMBER AT A RATE OF NOT LESS THAN ONE SAMPLE FOR EVERY 2500 SF IN EACH STORY
BOND STRENGTH @ FLOOR, ROOF, AND WALL ASSEMBLIES | 1705.13.6.1 | ASTM E736 | ONE FOR EACH FLOOR, ROOF, AND WALL ASSEMBLY EVERY 2500 SF OF SPRAYED AREA FOR EACH FLOOR LEVEL
SPRAYED FIRE-RESISTANT MATERIALS
BOND STRENGTH @ STRUCTURAL MEMBERS | 1705.13.6.2 | ASTM E736 | EACH TYPE OF STRUCTURAL MEMBER FOR EACH 2500 SF OF FLOOR AREA FOR EACH FLOOR LEVEL
MASTIC AND INTUMESCENT FIRE-RESISTIVE COATINGS
THICKNESS | 1705.14 | AWCI TECHNICAL MANUAL 12-B ASTM D1186 | ONE BAY PER FLOOR OR FOR EACH 10,000 SF OF FLOOR, WHICHEVER PROVIDES THE GREATEST NUMBER OF TESTS, TEST ONE COLUMN, ONE PRIMARY BEAM, ONE SECONDARY BEAM, AND ONE TRUSS
EXTERIOR INSULATION AND FINISH SYSTEMS, WATER-RESISTIVE BARRIER COATING
EXTERIOR INSULATION & FINISH SYSTEMS | 1705.15 | ASTM C297 ASTM D2247 ASTM D2898 ASTM E72 ASTM E96 ASTM E331 ASTM E1233 ASTM E2134 ASTM E2485 ASTM E2570 | See ASTM |  | A WATER-RESISTIVE BARRIER COATING COMPLYING WITH ASTM E 2570 REQUIRES SPECIAL INSPECTION OF THE WATER-RESISTIVE BARRIER COATING WHEN INSTALLED OVER A SHEATHING SUBSTRATE.

## Table 6
TABLE 6
REQUIRED SPECIAL INSPECTIONS for SEISMIC RESISTANCE (SEISMIC CATEGORIES C, D, E, F)
SYSTEM or MATERIAL | INSPECTION |  |  |  | REMARKS
| IBC CODE REFERENCE | CODE or STANDARD REFERENCE | FREQUENCY
|  |  | Continuous | Periodic
CONCRETE
CONCRETE SEISMIC-FORCE-RESISTING SYSTEMS (RISK CATEGORIES III & IV) | 1705.11 (1) |  | X (b)
REINFORCING STEEL PLACEMENT IN SPECIAL MOMENT RESISTING FRAMES AND BOUNDARY ELEMENTS OF SPECIAL STRUCTURAL WALLS AND SHEAR REINFORCEMENT | 1705.12.1 TABLE 1705.3 | ACI 318 1.3.5 AWS D 1.4 ACI 318 3.5.2 | X |  | INSPECTORS ARE TO BE QUALIFIED TO PERFORM THESE INSPECTIONS WHICH INCLUDES, BUT IS NOT LIMITED TO, THE PLACEMENT, STIRRUPS PLACEMENT, LAP LOCATION AND SPLICES, JOINT REINFORCEMENT PLACEMENT, ETC.
GROUTING OF BONDED POST TENSIONING TENDONS IN SEISMIC FORCE RESISTING SYSTEMS | 1705.11.1 TABLE 1705.3 | ACI 318: 18.18.1 ACI 318: 18.18.2 ACI 318: 18.18.3 ACI 318: 18.18.4 | X
MASONRY
MASONRY CONSTRUCTION | 1705.4 |  |  | X
STEEL
WELDING OF THE SEISMIC FORCE- RESISTING SYSTEM | 1705.11.1 | AISC 341 J6 AISC 360 AWS D1.8 | REFER TO TABLE 2 OF GUIDELINES FOR FABRICATOR AND WELDING SPECIAL INSPECTION REQUIREMENTS. ENGINEER OF RECORD TO CLEARLY INDICATE THE SCOPE OF INSPECTIONS ON DRAWINGS. IBC 1707.2 AND 1708.3 REQUIRE SPECIAL INSPECTIONS AND RELATED TESTING FOR STRUCTURAL STEEL FOR THE SEISMIC FORCE RESISTING SYSTEM TO COMPLY WITH THE QUALITY ASSURANCE PLAN REQUIREMENTS OF AISC 341. THE REGISTERED DESIGN PROFESSIONAL IN RESPONSIBLE CHARGE SPECIFIES THE QA PLAN WHICH SHOULD BE PROVIDED TO THE CONTRACTOR AS PART OF THE BID DOCUMENTS AND SHOULD BE CLEARLY IDENTIFIED AS SUCH. AISC RECOMMENDS THAT AISC 341 APPENDIX Q, “QUALITY ASSURANCE PLAN,” BE ADOPTED. AISC 341 INCLUDES COMMENTARY WHICH WILL BE HELPFUL TO ENGINEERS SPECIFYING PROJECT QA PLANS.
HIGH STRENGTH BOLT INSTALLATION IN THE SEISMIC FORCE-RESISTING SYSTEM | 1705.11.1 | AISC 341 J7 RCSC SPECIFICATION FOR STRUCTURAL JOINTS USING ASTM A325 OR A490 BOLTS | REFER TO TABLE 2 FOR HIGH STRENGTH BOLTING SPECIAL INSPECTION REQUIREMENTS
SEISMIC FORCE RESISTING FRAME SYSTEMS |  | AISC 341 J8 |  | X | SPECIAL INSPECTIONS APPLY TO CONTOUR, FINISH, AND DIMENSIONAL TOLERANCES
SEISMIC FORCE-RESISTING SYSTEM PROTECTED ZONES |  |  |  | X | SPECIAL INSPECTIONS APPLY TO VERIFYING THAT THERE ARE NO HOLES OR UNAPPROVED ATTACHMENTS INCLUDING UNACCEPTABLE WELDS IN PROTECTED ZONES
COLD-FORMED STEEL LIGHT-FRAMING
WELDING OF THE SEISMIC-FORCE-RESISTING SYSTEM | 1705.11.3 | AWS D1.3 SECTION 7 |  | X | ALL WELDS VISUALLY INSPECTED PER AWS D1.3 7.1
CONNECTIONS FOR DIAPHRAGM ATTACHMENT, DIAPHRAGM CHORDS, COLLECTORS AND BRACING, AND SHEAR WALL FASTENING, ANCHORAGE AND HOLDOWNS |  |  |  | X | ALL CONNECTIONS VISUALLY INSPECTED
PERIODIC SPECIAL INSPECTION IS REQUIRED DURING WELDING OPERATIONS OF ELEMENTS OF THE SEISMIC-FORCE-RESISTING SYSTEM. PERIODIC SPECIAL INSPECTION IS REQUIRED FOR SCREW ATTACHMENT, BOLTING, ANCHORING AND OTHER FASTENING OF COMPONENTS WITHIN THE SEISMIC-FORCE-RESISTING SYSTEM, INCLUDING SHEAR WALLS, BRACES, DIAPHRAGMS, COLLECTORS (DRAG STRUTS) AND HOLD-DOWNS. | 1705.11.3 | AWS D1.3 SECTION 7 |  | X (b) | ALL WELDS VISUALLY INSPECTED PER AWS D1.3 7.1 EXCEPTION: SPECIAL INSPECTION IS NOT REQUIRED FOR SHEAR WALLS, BRACES, DIAPHRAGMS, DRAG STRUT AND HOLDOWNS. IF SHEATHING IS GYP OR FIBERBOARD OR IF SHEATHING IS WOOD STRUCTURAL PANEL/STEEL SHEET ONE SIDE ONLY AND FASTENER SPACING IS GREATER THAN 4" ON CENTER.
STRUCTURAL WOOD
FIELD GLUING OF DIAPHRAGM AND SHEAR WALL ELEMENTS FOR SEISMIC FORCE-RESISTING-SYSTEMS | 1705.11.2 |  | X
CONNECTIONS FOR DIAPHRAGM CHORDS, COLLECTORS, BRACING, AND SHEAR WALL ANCHORAGE AND HOLDOWNS |  |  |  | X | ALL CONNECTIONS VISUALLY INSPECTED
FASTENING OF DIAPHRAGM AND SHEAR WALL SHEATHING WITH EDGE NAILING < 4" |  |  |  | X | SPECIAL INSPECTION IS NOT REQUIRED WHEN FASTENER SPACING IS GREATER THAN 4" ON CENTER FOR WOOD SHEAR WALLS, DIAPHRAGMS, NAILING, BUILDING AND OTHER COMPONENTS IN THE SEISMIC FORCE-RESISTING SYSTEM.
ARCHITECTURAL COMPONENTS
INSTALLATION OF ANCHORAGE OF ACCESS FLOORS | 1705.11.5.1 |  |  | X (a)
INSTALLATION OF ANCHORAGE OF CLADDING AND INTERIOR/EXTERIOR VENEER WEIGHING MORE THAN 5 PSF IN BUILDINGS MORE THAN 30 FEET IN HEIGHT | 1705.11.5 |  |  | X (a)
ERECTION AND FASTENING OF INTERIOR NONBEARING WALLS WEIGHING MORE THAN 15 PSF IN BUILDINGS MORE THAN 30 FEET IN HEIGHT | 1705.11.5 |  |  | X (a)
ERECTION AND FASTENING OF EXTERIOR NON-BEARING WALLS IN BUILDINGS MORE THAN 30 FEET IN HEIGHT | 1705.11.5 |  |  | X (a)
INSTALLATION OF ANCHORAGE OF STORAGE RACKS WITH Ip = 1.5 | 1705.11.7 | ASCE 7-10 Section 15.5.3 |  | X (a)
INSTALLATION AND ANCHORAGE OF SUSPENDED CEILING SYSTEMS | 1705.11 | ASCE 7-10 Section 13.5.6 |  | X (a)
INSTALLATION OF OTHER SEISMIC SUPPORTS FOR DESIGNATED ARCHITECTURAL SYSTEMS AND THEIR COMPONENTS | 1705.11.5 |  |  | X (a)
ELECTRICAL COMPONENTS
INSTALLATION OF ANCHORAGE OF ELECTRICAL EQUIPMENT FOR EMERGENCY OR STANDBY POWER SYSTEMS | 1705.11.6 |  |  | X (a)
INSTALLATION OF ANCHORAGE OF ALL ELECTRICAL EQUIPMENT IN SDC E OR F ONLY | 1705.11.6 |  |  | X (a)
INSTALLATION OF VIBRATION ISOLATION SYSTEMS IN STRUCTURES ASSIGNED TO SDC C, D, E OR F WHERE THE CONSTRUCTION DOCUMENTS REQUIRE A NOMINAL CLEARANCE OF 0.25 INCHES OR LESS BETWEEN THE EQUIPMENT SUPPORT FRAME AND RESTRAINT | 1705.11.6 |  |  | X (a)
INSTALLATION OF OTHER SEISMIC SUPPORTS FOR DESIGNATED ELECTRICAL SYSTEMS AND THEIR COMPONENTS | 1705.11.6 |  |  | X (a)
PROCESS MECHANICAL COMPONENTS
INSTALLATION OF PIPING SYSTEM MEANT TO CARRY FLAMMABLE, COMBUSTIBLE OR HIGHLY TOXIC CONTENTS AND ITS ASSOCIATED MECHANICAL UNITS | 1705.11.6 |  |  | X (a)
INSTALLATION OF OTHER SEISMIC SUPPORTS FOR DESIGNATED MECHANICAL SYSTEMS AND THEIR COMPONENTS | 1705.11.6 |  |  | X (a)
BUILDING MECHANICAL COMPONENTS
INSTALLATION OF HVAC DUCTWORK THAT WILL CONTAIN HAZARDOUS MATERIALS | 1705.11.6 |  |  | X (a)
DESIGNATED SEISMIC SYSTEM VERIFICATION
DESIGNATED SEISMIC SYSTEM VERIFICATION - VERIFY LABEL, ANCHORAGE OR MOUNTING CONFORMS TO THE CERTIFICATE OF COMPLIANCE | 1705.11.4 |  |  | X (a) | REGISTERED DESIGN PROFESSIONAL SHALL IDENTIFY INSPECTION POINTS, FREQUENCY, TYPE AND EXTENT OF SPECIAL INSPECTIONS. VERIFY THAT THE LABEL, ANCHORAGE OR MOUNTING CONFORMS TO THE CERTIFICATE OF COMPLIANCE.

## Table 7
TABLE 7
REQUIRED TESTING for SEISMIC RESISTANCE SPECIAL INSPECTIONS
SYSTEM or MATERIAL | TESTING |  |  |  | REMARKS
| IBC CODE REFERENCE | CODE or STANDARD REFERENCE | FREQUENCY
|  |  | Continuous | Periodic
CONCRETE REINFORCEMENT
TEST A615 REINFORCEMENT USED TO RESIST EARTHQUAKE INDUCED LOAD IN SPECIAL MOMENT FRAMES, SPECIAL STRUCTURAL WALLS, AND END COUPLING BEAMS CONNECTING STRUCTURAL WALLS IN STRUCTURE ASSIGNED TO SEISMIC DESIGN CATEGORY B, C, D, E AND F | 1705.12.1 | ACI 318: 21.1.5.2 | X (b) | X (a) | NOT REQUIRED WHEN CERTIFIED MILL TEST REPORTS ARE PROVIDED
TEST A615 REINFORCEMENT FOR WELDABILITY WHEN SUCH REINFORCEMENT IS TO BE WELDED | 1705.12.1 | ACI 318: 3.5.2 |  | X (a)
STEEL
UT OF BASE METAL THICKER THAN 1-1/2" SUBJECT TO THROUGH-THICKNESS WELD SHRINKAGE STRAINS | 1705.12.2 | AISC 341 J6.2c AWS D1.8 AWS D1.1 | BEHIND AND ADJACENT TO FUSION LINE OF EACH WELD |  | IBC 1705.11.1 AND 1705.12.2 REQUIRE SPECIAL INSPECTIONS AND RELATED TESTING FOR STRUCTURAL STEEL FOR THE SEISMIC FORCE RESISTING SYSTEM TO COMPLY WITH THE REQUIREMENTS OF AISC 341. THE REGISTERED DESIGN PROFESSIONAL IN RESPONSIBLE CHARGE SPECIFIES THE QA PLAN WHICH SHOULD BE PROVIDED TO THE CONTRACTOR AS PART OF THE BID DOCUMENTS AND SHOULD BE CLEARLY IDENTIFIED AS SUCH. AISC RECOMMENDS THAT AISC 341 CHAPTER J, "QUALITY CONTROL AND QUALITY ASSURANCE" BE ADOPTED. AISC 341INCLUDES COMMENTARY WHICH WILL BE HELPFUL TO ENGINEERS SPECIFYING PROECT QA PLANS.
MT OF K-AREA OF ROLLED WIDE FLANGE COLUMN WEBS ADJACENT TO DOUBLER/CONTINUITY/STIFFENER PLATE WELDS | 1705.12.2 | AISC 341 J6.2a AWS D1.8 AWS D1.1 | EACH PLATE LOCATION
MAGNETIC PARTICLE (MT) AND ULTRASONIC (UT) TESTING OF COMPLETE JOINT PENETRATION GROOVE (CJP) WELDS IN MATERIALS 5/16" THICK AND GREATER | 1705.12.2 | AISC 341 J6.2b AWS D1.8 AWS D1.1 | UT 100% OF WELDS MT 25% OF WELDS REFER TO DRAWINGS FOR LOCATIONS
PT OR MT OF THERMALLY CUT SURFACES OF BEAM COPES AND ACCESS HOLES AT WELDED SPLICES AND CONNECTIONS WHEN THE FLANGE THICKNESS EXCEEDS 1 1/2" FOR ROLLED SHAPES OR THE WEB THICKNESS EXCEEDS 1 1/2" FOR BUILT-UP SHAPES | 1705.12.2 | AISC 341 J6.2d AWS D1.8 AWS D1.1 | EACH LOCATION
MT OF THE WELD AND ADJACENT AREA IN A REDUCED BEAM SECTION (RBS) PLASTIC HINGE REGION REPAIRED BY WELDING OR BY GRINDING OF SHARP NOTCHES | 1705.12.2 | AISC 341 J6.2e AWS D1.8 AWS D1.1 | EACH LOCATION
MT OF THE ENDS OF FLANGE WELDS FROM WHICH WELD TABS HAVE BEEN REMOVED | 1705.12.2 | AISC 341 J6.2f AWS D1.8 AWS D1.1 | EACH TESTED CJP WELD LOCATION
ARCHITECTURAL, MECHANICAL AND ELECTRICAL COMPONENTS
PROJECT-SPECIFIC DESIGN OR COMPONENT TESTING INCLUDING MOUNTING SYSTEMS OR ANCHORAGE IF CERTIFICATES OF COMPLIANCE ARE NOT AVAILABLE | 1705.12 1705.12.3 | ASCE 7 - SECTION 13.2.1 |  | X (a) | WHEN REQUIREMENTS OF 13.2.1 ARE MET BY SUBMITTAL OF MANUFACTURER'S CERTIFICATION, THE REGISTERED DESIGN PROFESSIONAL SHALL SPECIFY ON THE CONSTRUCTION DOCUMENTS THE REQUIREMENTS FOR CERTIFICATION.
SEISMICALLY ISOLATED STRUCTURES
SYSTEM TESTS | 1705.12.4 | ASCE 7 - 17.8 |  | X (a)
DESIGNATED SEISMIC SYSTEMS
COMPONENT CERTIFICATION BY ANALYSIS, TESTING OR EXPERIENCE DATA WHEN Ip>1.0 | 1705.12.3 | ASCE 7 13.2.2 |  | X (a) | THE REGISTERED DESIGN PROFESSIONAL SHALL SPECIFY ON THE CONSTRUCTION DOCUMENTS THE REQUIREMENTS FOR CERTIFICATION.

## Table 8
TABLE 8
REQUIRED SPECIAL INSPECTIONS for WIND RESISTANCE
SYSTEM or MATERIAL | INSPECTION |  |  |  | REMARKS
| IBC CODE REFERENCE | CODE or STANDARD REFERENCE | FREQUENCY
|  |  | Continuous | Periodic
NAILING, BOLTING, ANCHORING AND OTHER FASTENING OF COMPONENTS WITHIN THE MAIN WINDFORCE-RESISTING SYSTEM, INCLUDING WOOD SHEAR WALLS, WOOD DIAPHRAGMS, DRAG STRUTS, BRACES AND HOLD-DOWNS | 1705.10.1 |  |  | X (a) | SPECIAL INSPECTIONS ARE NOT REQUIRED FOR WOOD SHEAR WALLS AND DIAPHRAGMS WHERE THE FASTENER SPACING IS MORE THAN 4 INCHES ON CENTER OR FOR COLD-FORMED CONSTRUCTION WHERE THE SHEATHING IS GYPSUM BOARD, FIBERBOARD, OR WOOD STRUCTURAL PANEL OR STEEL SHEET ON ONE SIDE ONLY AND FASTENER SPACING IS MORE THAN 4" O.C.
FIELD GLUING OPERATIONS OF ELEMENTS OF THE MAIN WIND-FORCE-RESISTING SYSTEM. | 1705.10.1 |  | X
COLD-FORMED STEEL LIGHT-FRAME CONSTRUCTION | 1705.10.2 |  |  | X (a) | SPECIAL INSPECTIONS ARE REQUIRED FOR WELDING OPERATIONS OF ELEMENTS OF THE MAIN WIND FORCE-RESISTING SYSTEM. SPECIAL INSPECTION IS REQUIRED FOR SCREW ATTACHMENT, BOLTING, ANCHORING AND OTHER FASTENING OF COMPONENTS WITHIN THE MAIN WIND-FORCE-RESISTING SYSTEM, INCLUDING SHEAR WALLS, BRACES, DIAPHRAGMS, COLLECTORS AND HOLD DOWNS.
ROOF CLADDING AND WALL CLADDING | 1705.10.3 |  |  | X (a)

## Table 9
TABLE 9
STRUCTURAL OBSERVATION
SYSTEM or MATERIAL | INSPECTION |  |  |  | REMARKS
| IBC CODE REFERENCE | CODE or STANDARD REFERENCE | FREQUENCY
|  |  | Continuous | Periodic
AS REQUIRED BY THE DESIGN PROFESSIONAL | 1704.5
SEISMIC RESISTANCE | 1704.5.1 |  |  | X (a) | SEE COMMENTARY
WIND REQUIREMENTS | 1704.5.2 |  |  | X (a) | SEE COMMENTARY