This table addresses special inspections for non-structural work.

Spray-Applied Fire Resistive Material (SFRM)

Special inspection should be based upon the fire resistance design as designated in the approved construction documents. The special inspector should review and understand the approved design.  Inspections include verification of prepared surface conditions and proper application procedures and ambient conditions.  The completed work should be inspected to be sure that there are no bare spots or pockets.  Technical Manual 12-A published by AWCI provides useful background information.  Testing requirements related to these special inspections, which are listed in detail in guideline Table 5, have been incorporated into the 2014 OSSC in 1705.13.

Mastic & Intumescent Fire-Resistive Coatings

These materials are Thin-Film Intumescent Fire-Resistive Materials (TFIFRM) and are applied to structural members at thicknesses not greater than 300mils.  Per 2014 OSSC, special inspections shall be based upon the fire resistance design as designated in the approved construction documents and in accordance with AWCI 12-B.  See guideline Table 5 for related testing requirements.

Exterior Insulation and Finish Systems

The special inspector shall review the installation, preparation, method of moisture drainage and application for compliance with the approved construction documents.  The system should be specified in the specifications and field verified.  The scope of the special inspection should be in the SI/T/SO program by the registered Design Professional.

Smoke Control Systems

The special inspector shall review the testing, detection and control prior to occupancy.

Fire-Resistant Penetrations and Joints

The special inspector shall verify that the systems and construction conform to the systems tested and listed as specified.

Radon Mitigation Inspections

Where radon mitigation systems are required by Section 1811 of this code, special inspections shall be provided per the methods and frequency in Section 1705.18.